## Slide 1: Produced Water Quality Standards & Techno-economic Analysis for Alternative Treatment Trains
Nick Tiwari, Chad Able and Tommy Schmitt
NETL support contractors
September 26, 2024
September 24, 2021
Interim Results
Notes: SA-2 Activity 9 Task 4-1

## Slide 2: Agenda
Objectives
Design Basis
  Stream input data
  Quality standards
Process Description
  Summary of process components
  Nanofiltration and membrane distillation unit ops
Results
Future work
  QGESS costing module

## Slide 3: Objectives
Identify an acceptable water quality standard
  Federal drinking water standards
  Non-potable reclaimed water standards
    Firefighting, irrigation of public parks, agriculture
Propose water treatment trains to purify produced water
  Minimum cost and energy expense
Evaluate treatment trains based on cost and effectiveness
Provide recommendations based upon relevant results
Develop additional software tools to improve accuracy and usability
  QGESS costing module

## Slide 4: Stream input data
With a focus in the Permian Basin, the median data generated in prior work from the National Energy Water Treatment and Speciation database can be reused (critical minerals in bold)
This has additionally been reconciled in OLI Studio (treating boron as B(OH)3 and Si as SiO2), producing a final total dissolved solids (TDS) of 99,302 mg/L (the reconciled TDS will be used)
Parameter Name | Median Value
TDS, mg/L | 101,336
Ammonia, mg/L | 96
Barium, mg/L | 2.355
Boron, mg/L | 19.51
Bicarbonate, mg/L | 231.005
Bromine, mg/L | 224
Calcium, mg/L | 3,127.5
Carbonate, mg/L | 48.885
Chlorides, mg/L | 59,200
Iodine, mg/L | 10
Iron, mg/L | 21
Lithium, mg/L | 10.75
Magnesium, mg/L | 889.115
Manganese, mg/L | 0.885
Potassium, mg/L | 402.87
Silicon, mg/L | 12
Sodium, mg/L | 31,275
Strontium, mg/L | 123.755
Sulfate, mg/L | 1,438.375
Parameter Name | Median Value
Depth (upper), ft | 6749
Depth (lower), ft | 7408
Depth (well), ft | 7020
Elevation, ft | 2895.5
Temperature, F | 143.45
pH, SU | 6.95
Specific gravity | 1.077
Resistivity, Ohm m | 0.086
Conductivity, μS/cm | 138,000

## Slide 5: Water quality standards
Federal drinking water standards
Level I reclaimed water, according to the Texas Administrative Code §210.53

## Slide 6: Process description
Pretreatment
Primary Treatment
Secondary Treatment
Influent
Effluent
Ion Exchange (IX)
Nanofiltration (NF)
Membrane Distillation (MD)
Low salt rejection reverse osmosis (LSRRO)
Osmotically Assisted Reverse Osmosis (OARO)
Crystallization

## Slide 7: Process description
Pretreatment
Primary Treatment
Secondary Treatment
Influent
Effluent
Ion Exchange (IX)
Nanofiltration (NF)
Membrane Distillation (MD)
Low salt rejection reverse osmosis (LSRRO)
Osmotically Assisted Reverse Osmosis (OARO)
Crystallization

## Slide 8: Nanofiltration (NF)
Driven by hydrostatic pressure difference
Capable of filtering particles 1-10 Å in size
WaterTAP model
  Assumed performance model
  Donnan Steric Pore Model (DSPM)
Water professionals. WaterProfessionals®. (n.d.). https://www.waterprofessionals.com/learning-center/nanofiltration/

## Slide 9: Nanofiltration – assumed performance model
Performance is based on the user’s specification, not on physics/thermodynamics
2 DOF
  Mass fraction of components in inlet feed (xf,i)
  Mass fraction of solute rejected by membrane (xr,i)
Pros
  Easy to set up
  Quick to simulate
  Highly flexible
Cons
  Lack of physical basis makes potential for error much higher
  Related process parameters aren’t affected by change in performance variable
Permeate
Feed
Reject

## Slide 10: Donnan Steric Pore Model
Based on Nernst-Planck equations
  NP describes mass transport of a charged species in fluid
Pros
  Underlying physics describe performance
Cons
  Requires more time to solve than assumed performance
    We’re solving a non-linear ordinary differential equation (finite-difference method)
Geraldes, V., & Brites Alves, A. M. (2008). Computer Program for simulation of mass transport in nanofiltration membranes. Journal of Membrane Science, 321(2), 172–182. https://doi.org/10.1016/j.memsci.2008.04.054

## Slide 11: Donnan Steric Pore Model
Geraldes, V., & Brites Alves, A. M. (2008). Computer Program for simulation of mass transport in nanofiltration membranes. Journal of Membrane Science, 321(2), 172–182. https://doi.org/10.1016/j.memsci.2008.04.054
Ji | Solute flux | ci | Ion concentration
Jv | Permeate volume flux | zi | Ion valence
Di,p | Hindered diffusion coefficient | RT | Thermal energy
Ki,c | Convection hindrance coefficient | ψ | Electrostatic potential
F | Faraday constant |  | 
Diffusion
Advection
Electromigration

## Slide 12: Donnan Steric Pore Model
Geraldes, V., & Brites Alves, A. M. (2008). Computer Program for simulation of mass transport in nanofiltration membranes. Journal of Membrane Science, 321(2), 172–182. https://doi.org/10.1016/j.memsci.2008.04.054
Ji | Solute flux | ci | Ion concentration
Jv | Permeate volume flux | zi | Ion valence
Di,p | Hindered diffusion coefficient | RT | Thermal energy
Ki,c | Convection hindrance coefficient | ψ | Electrostatic potential
F | Faraday constant |  | 
Diffusion
Advection
Electromigration
Discretization

## Slide 13: Membrane distillation (MD)
Membrane is hydrophobic
  Water contact angle > 90°
Liquid cannot pass through pores
  Any water that is present is in the vapor phase
Vapor pressure of metals/salts at normal operating conditions (below several hundred Celcius) is extremely low
  Almost no solute should pass through
Vapor pressure difference arises due to temperature change
  This is the driving force
Notes: The standards may be more about temperature, pressure, etc. rather than the value of specific constituents. Assuming there are no standards for those applications, the analysis would default to federal drinking water standards.

## Slide 14: Membrane distillation (MD) – WaterTAP process model
Process components
  Heater
  Cooler
  Heat Exchanger
  MD unit
Total process cost incorporates individual costs for all process components
Notes: The standards may be more about temperature, pressure, etc. rather than the value of specific constituents. Assuming there are no standards for those applications, the analysis would default to federal drinking water standards.

## Slide 15
Results

## Slide 16: A sample flowsheet/stream table

## Slide 17: Normalized water cost and energy consumption

## Slide 18: Total operating and capital cost
LCOW is generally dominated by operating costs, not capital costs
  Utility requirements (e.g. heating and cooling duty)

## Slide 19: TOC relative to TCC
TOC exceeds TCC only for:
  Low fractional recovery
  High membrane area
This is reasonable given that large membranes should be both more expensive and better at purification

## Slide 20
Future work

## Slide 21: QGESS costing implementation
WaterTAP has a dedicated costing method
Very simple – often just sizes equipment based on a single parameter (i.e. membrane size)
Through modification of the QGESS costing class provided in PrOMMIS, we can add this functionality to
Assumed QGESS costing parameters
Scaling parameter

## Slide 22: Questions/ Comments
Alison Fritz
Alison.Fritz@netl.doe.gov
Notes: Photo: 3-D printing of NETL logo in the Multiphase Flow Analysis Laboratory at NETL Morgantown